## Disclaimer
Classroom CO2 Decay Measurement and Ventilation Rate Calculation Datasheet (using English units)
Disclaimer: This spreadsheet is for illustrative purposes only based on the inputs that a user enters in the tab of "Example datasheet". It demonstrates how to estimate outdoor air ventilation rates (VRs) based on classroom CO2 decay measurement. For details of how to conduct a CO2 decay test, see Appendix E of the IAQ report entitled "Ventilation and Filtration to Reduce Long-range Airborne Transmission of COVID-19 and Other Respiratory Infections: Considerations for Reopened Schools."

## Example datasheet
Information to be entered by field inspector (or user): Enter (or overwrite) the values in the "User Input" column and in cells B2 and D2 to calculate your VR
Inspector's name: | Jane Jones | Date: | 2021-01-21
Category | Parameter | User input | Units | Note
Classroom information | Classroom name | 101 | n/a | Enter classroom name or number
Classroom information | Floor area | 960 | ft2 | Measure and enter floor area
Classroom information | Ceiling height | 9 | ft | Measure and enter average ceiling height
Classroom information | Number occupants | 27 | person | Enter expected maximum number of occupants
CO2 monitor reading | Coutdoor initial | 433 | ppm | Enter initial outdoor CO2 concentration; if not measured, assume 400 ppm
Measurement time | T1 | 10:14 | h:min | Enter time Coutdoor initial measured
CO2 monitor reading | Cindoor initial | 1063 | ppm | Enter initial indoor CO2 concentration
Measurement time | T2 | 10:37 | h:min | Enter time Cindoor initial measured
CO2 monitor reading | Cindoor final | 546 | ppm | Enter final indoor CO2 concentration
Measurement time | T3 | 11:07 | h:min | Enter time Cindoor final measured
CO2 monitor reading | Coutdoor final | 449 | ppm | Enter final outdoor CO2 concentration; if not measured, assume 400 ppm
Measurement time | T4 | 11:23 | h:min | Enter time Coutdoor final measured

## Example calculations
Calculated Values based on Example Datasheet
Category | Parameter | Calculated value | Units | Note
Classroom information | Volume | 8640 | ft3 | Calculated as (Floor area ´ Ceiling height)
CO2 concentration | Coutdoor average | 441 | ppm | Calculated as average of Coutdoor initial and Coutdoor final
CO2 concentration | Cindoor initial − Coutdoor average | 622 | ppm | Initial indoor concentration after background subtraction
CO2 concentration | Cindoor final − Coutdoor average | 105 | ppm | Final indoor concentration after background subtraction
CO2 concentration | (Cindoor final − Coutdoor average)/ (Cindoor initial − Coutdoor average) | 0.16881 | unitless | Ratio of corrected final to initial indoor concentration
Measurement time | T3 – T2 | 30 | min | Time used for VR calculation

## Example estimated VR
Estimated VR: Model Outputs
Category | Parameter | Calculated value | Units
Estimated VR | Outdoor air change rate (ACH) | 3.558 | h-1 (or ACH)
Estimated VR | Outdoor airflow rate | 512.3462 | cfm
Estimated VR | Outdoor airflow rate per occupant | 18.9758 | cfm/occupant
Estimated VR | Outdoor airflow rate per floor area | 0.53369 | cfm/ft2